## Test 3
Part A
Component | Variable | Value | Unit | Value | Unit
Flow Rate | Q | 0.6127 | ft3/s | 275 | gpm
Resistance Coefficient | KEntrance | 0.5 | Ft
| KElbow | 30 | Ft
| KGate Valve | 8 | Ft | Full Open | 8
| KCheck Valve | 100 | Ft | 3/4 Open | 35
| KHeat Exchanger | 12 | Ft | 1/2 Open | 160
| Kpipe Tee | 60 | Ft | 1/4 Open | 900
| Kred 4"/ 3" | _ | _
| Kred 3"-1" | _ | _
| KEnlarge 1"-2" | _ | _
Water @ 160 °F | γ | 61 | lb/ft3
| p | 1.9 | slug/ft3
| n | 8.3e-06 | lb-s/ft2
| v | 4.38e-06 | ft2/s
Schedule 40 Pipe | ϵ | 0.00015 | ft
1in Pipe | ID | 0.0874 | ft
| Area | 0.006 | ft2
| (30ft) L/D | 343.2494 | _
| D/ϵ | 582.6667 | _
| Re | 2037680.449 | _
| f | 0.022647 | _
| Ft | 0.022496 | _
| velocity V=Q/A | 102.1172 | ft/s2
3in Pipe | ID | 0.2557 | ft
| Area | 0.05132 | ft2
| (48ft) L/D | 187.72 | _
| D/ϵ | 1704.6667 | _
| Re | 696979.4552
| f | 0.018057 | _
| Ft | 0.017314 | _
| velocity V=Q/A | 11.9389 | ft/s2
4in Pipe | ID | 0.3355 | ft
| Area | 0.0884 | ft2
| (10ft) L/D | 29.8063 | _
| D/ϵ | 2236.6667 | _
| Re | 530904.1935 | _
| f | 0.017381 | _
| Ft | 0.016288 | _
| velocity V=Q/A | 6.931 | ft/s2
Gravity | g | 32.2 | ft/s2
Pump Efficiency | PEff | 0.7 | _
Height | Z2-Z1 | 10.5 | _
Branch 1 |  |  |  | Quantity | Total
(3") hL Pipe Bend 900 hL=K Pipe Bend(V22/2g) | K*(V22/2g) | 1.1497 | ft | 4 | 4.5987
|  |  |  | Quantity | Total
(3") hL Pipe Tee hL=K Pipe Tee(V22/2g) | K*(V22/2g) | 2.2993 | ft | 2 | 4.5987
|  |  |  | Quantity | Total
(3") hL Check Valve hL=K Check Valve(V22/2g) | K*(V22/2g) | 3.8322 | ft | 1 | 3.8322
|  |  |  | Quantity | Total
(3") hL Overall Pipe hL=ff*(L/D)*(V22/2g) | hL=ff*(L/D)*(V22/2g) | 7.5025 | ft | 1 | 7.5025
|  |  |  | Quantity | Total
(3-2") hL Reduction hL=K Red (V22/2g) | K*(V22/2g) | 17.7064 | ft | 3 | 53.1193
|  |  |  | Quantity | Total
(3") hL Gate Valve hL=K Gate Valve(V22/2g) | K*(V22/2g) | 0.30658 | ft | 3 | 0.91973
|  |  |  | Quantity | Total
(4") hL Gate Valve hL=K Gate Valve(V22/2g) | K*(V22/2g) | 0.097197 | ft | 1 | 0.097197
|  |  |  | Quantity | Total
(4") hL Suction Line hL=ff*(L/D)*(V22/2g) | hL=ff*(L/D)*(V22/2g) | 0.38645 | ft | 1 | 0.38645
|  |  |  | Quantity | Total
(4") hL Pipe Bend 900 hL=K Pipe Bend(V22/2g) | K*(V22/2g) | 0.36449 | ft | 0 | 0
|  |  |  | Quantity | Total
hL Entrance Loss hL=K Square Inlet(V22/2g) | hL=K Entrance Loss(V22/2g) | 0.37297 | ft | 1 | 0.37297
2.1931
|  |  |  | Quantity | Total
(1") hL Pipe Bend 900 hL=K Pipe Bend(V22/2g) | K*(V22/2g) | 109.2799 | ft | 0 | 0
|  |  |  | Quantity | Total
(1") hL Gate Valve hL=K Gate Valve(V22/2g) | K*(V22/2g) | 29.1413 | ft | 1 | 29.1413 | Full Open
|  |  |  | Quantity | Total
(1") hL Overall Pipe hL=ff*(L/D)*(V22/2g) | hL=ff*(L/D)*(V22/2g) | 1258.7334 | ft | 1 | 1258.7334
|  |  |  | Quantity | Total
hL Heat Exchanger hL=K(V22/2g) | hL=K HX Loss(V22/2g) | 26.5596 | ft | 1 | 26.5596
[6 empty] | Part A hL Total (ft) | 48.868
|  |  |  | Quantity | Total
hA | hA=(Z1 - Z2)V2/2g+hL | 72.1077 | ft | _ | _
PA | PA=hAYQ/550 | 4.9 | hp | _ | _
2695.017
Pump Efficiency | PI=PA/PEff | 7 | hp | _ | _
Part B
[8 empty] | Pipe | Value | f Value |  | Heights
PA | PA=hAYQ | 2695.017 | hp | _ | _ |  |  | 4" | 1.987 | 0.0174 |  | Z1 | 4.5
[8 empty] | 3" | 5.888 | 0.0181 |  | Z2 | 15
[8 empty] | 1" | 431.4 | 0.0026 |  | Delta Z | 10.5
Resistance Coefficient | KEntrance | 0.5 | Ft
| KElbow | 30 | Ft
| KGate Valve | 8 | Ft | Full Open | 8
| KCheck Valve | 100 | Ft | 3/4 Open | 35
| KHeat Exchanger | 12 | Ft | 1/2 Open | 160
| Kpipe Tee | 60 | Ft | 1/4 Open | 900
| Kred 4"/ 3" | _ | _
| Kred 3"-1" | _ | _
| KEnlarge 1"-2" | _ | _
BRANCH 1 |  | hL |  | Quantity | Total
hL Entrance Loss hL=K Square Inlet(V22/2g) | hL=K Entrance Loss(V22/2g) | 0.9935 | ft | 1 | 0.9935
|  |  |  | Quantity | Total
(4") hL Gate Valve hL=K Gate Valve(V22/2g) | K*(V22/2g) | 0.27659 | ft | 1 | 0.27659
|  |  |  | Quantity | Total
(3") hL Check Valve hL=K Check Valve(V22/2g) | K*(V22/2g) | 10.6573 | ft | 1 | 10.6573
|  |  |  | Quantity | Total
(3") hL Gate Valve hL=K Gate Valve(V22/2g) | K*(V22/2g) | 0.85258 | ft | 3 | 2.5577
|  |  |  | Quantity | Total
(3") hL Pipe Bend 900 hL=K Pipe Bend(V22/2g) | K*(V22/2g) | 3.1972 | ft | 4 | 12.7887
|  |  |  | Quantity | Total
(3") hL Pipe Tee hL=K Pipe Tee(V22/2g) | K*(V22/2g) | 6.3944 | ft | 2 | 12.7887
|  |  |  | Quantity | Total
hL Heat Exchanger hL=K(V22/2g) | hL=K HX Loss(V22/2g) | 70.656 | ft | 1 | 70.656
|  |  |  | Quantity | Total
(4") hL Suction Line hL=ff*(L/D)*(V22/2g) | hL=ff*(L/D)*(V22/2g) | 1.0305 | ft | 1 | 1.0305
|  |  |  | Quantity | Total
(3") hL Overall Pipe hL=ff*(L/D)*(V22/2g) | hL=ff*(L/D)*(V22/2g) | 20.0058 | ft | 1 | 20.0058
hL A-B Total Branch 1 | 131.7549
Q (ft^3/s | 0.63465 |  |  |  | hL Branch 1 to Tee | 15.9419
Q (gpm) | 284.8528
BRANCH 2 |  | hL |  | Quantity | Total
hL Entrance Loss hL=K Square Inlet(V22/2g) | hL=K Entrance Loss(V22/2g) | 0.9935 | ft | 1 | 0.9935
|  |  |  | Quantity | Total
(4") hL Gate Valve hL=K Gate Valve(V22/2g) | K*(V22/2g) | 0.27659 | ft | 1 | 0.27659
|  |  |  | Quantity | Total
(3") hL Gate Valve hL=K Gate Valve(V22/2g) | K*(V22/2g) | 0.85258 | ft | 1 | 0.85258
|  |  |  | Quantity | Total
(1") hL Pipe Bend 900 hL=K Pipe Bend(V22/2g) | K*(V22/2g) | 33.6492 | ft | 2 | 67.2984
|  |  |  | Quantity | Total
(3") hL Pipe Tee hL=K Pipe Tee(V22/2g) | K*(V22/2g) | 6.3944 | ft | 2 | 12.7887
|  |  |  | Quantity | Total
(4") hL Suction Line hL=ff*(L/D)*(V22/2g) | hL=ff*(L/D)*(V22/2g) | 1.0305 | ft | 1 | 1.0305
|  |  |  | Quantity | Total
(1") hL Overall Pipe hL=ff*(L/D)*(V22/2g) | hL=ff*(L/D)*(V22/2g) | 385.0023 | ft | 1 | 385.0023
|  |  |  | Quantity | Total
(1") hL Gate Valve hL=K Gate Valve(V22/2g) | K*(V22/2g) | 8.9731 | ft | 1 | 8.9731
hL A-B Total Branch 2 | 477.2157
Q2 lower (ft^3/s | 0.41326
Q (gpm) | 185.4832
Q1 upper (ft^3/s | 0.63465
Q (gpm) | 284.8528 | [5 empty] | LHS | RHS
[7 empty] | 470.336 | 470.336
Conservation of Mass Q3=Q1+Q2 | 470.336
If "K" value was swapped in gate valve branch 2
Don’t think I need
[6 empty] | Iteration | Position | K | Q1 | f | Q2 | RHS | % diff | Q gpm
Unfortunately ran out of time, I don’t think I did this part correctly, could not get my right and side to add up correctly | [5 empty] | 0 | Closed | 0 | 0.0111 |  |  | 0.10874 | 0 | 48.8041 | Q2
[6 empty] | 1 | Full Open | 8 | 0.63465 |  | 0.41326 | 0.10874 | #DIV/0! | 48.8041 |  | 185.4832
[6 empty] | 2 | 3/4 Open | 35 | _ |  |  | 0.10874 | #DIV/0! | 48.8041 |  | 181.7178
[6 empty] | 3 | 1/2 Open | 160 | _ |  |  | 0.10874 | #DIV/0! | 48.8041 |  | 167.527
[6 empty] | 4 | 1/4 Open | 900 | _ |  |  | 0.10874 | #DIV/0! | 48.8041 |  | 127.256
𝑓_𝑇=0.25/[log(1/3.7(𝐷/𝜀) )]^2
𝑅𝑒=𝑉𝐷/𝜈
𝑓=0.25/[log(1/3.7(𝐷/𝜀) +5.74/〖𝑅𝑒〗^0.9 )]^2
𝑝_1/𝛾+𝑧_1+(𝑣_1^2)/2𝑔−ℎ_𝐿+ℎ_𝐴=𝑝_2/𝛾+𝑧_2+(𝑣_2^2)/2𝑔
%diff=(LHS−RHS)/LHS×100
𝑓=0.25/[log(1/3.7(𝐷/𝜀) +5.74/〖𝑅𝑒〗^0.9 )]^2